DESIGN AND CONSTRUCTION OF 1KVA UNINTERRUPTED POWER SYSTEM (UPS)

ABSTRACT

A UPS system is a DC to AC conversion system of 1KVA power rating and expected to carry around 800 watts load. It provides power to electronic and electrical appliances such as radio sets, TV DVD/VCD, computers, fans and lighting. The design was conceived and put down as block diagram. Corresponding circuit diagrams for each black box were sourced and drawn. The component values according to desired specifications were designed from the first principle and needed values derived. The transformer was also designed and with measurements and component values we went to the market. Most of the transistors were not in the market and order was made with the trader and they were later collected. These components were first wired on project board, tested before being removed and transferred to veroboard where they were soldered permanently and tested. The tests carried out were successfully including the capacity of the transformer and the transformer stability and hum-free operation. The circuit veroboard and transformer along with meters, switches, indicators and output sucket were all carefully packaged inside the system box and test carried out again. This financial test was also successful

TABLE OF CONTENTS

Title 										Page

Title Page  									i

Certification 									ii

Dedication									iii

Acknowledgement  								iv

Abstract 										v

Table of Contents 								vi

List of tables 									ix

List of Figures 									x

List of Appendices 								ix

CHAPTER ONE

INTRODUCTION 								1

1.1	The Background of the Problem				1

1.2	The Purpose/Objective/Aim of the Project 		2

1.3	Scope of the Project 						3

1.4	Limitation of the Study 						4

1.5	Definition of operational Terms: 				5

CHAPTER TWO

LITERATURE REVIEW 							9

  - Feedback Oscillator principle					10

  - Astable Multivibrator Principle				11

  - Field Effect Transistor (FET)					14

CHAPTER THREE

DESIGN METHODOLOGY 						18

3.1	Block diagram/flow chart of UPS				19

3.2	Specification 								20

CHAPTER FOUR

ANALYSIS AND DESIGN							21

4.1	Voltage regulator/monitor					21

4.2	UPS circuit								23

4.3	Low pass filter 								25

4.4	Pre-amplifier 								26

4.5	Buffer amplifier 							28

4.6	Power amplifier 							30

4.7	Heat sink 								32

4.8	UPS transformer design						32

4.9	Complete circuit diagram of 1kva ups system with built 12VDC battery								44

CHAPTER FIVE

PRESENTATION AND ANALYSIS OF RESULT 		45

5.1	Construction, testing and packaging 			47

CHAPTER SIX

CONCLUSION AND RECOMMENDATION 			52

6.1	Conclusion 								52

6.2	Recommendation 							52

References 								54

Appendix I								55

Appendix II								57

LIST OF TABLES

Table 4.1:		Coefficient of Utilization 				35

Table 4.2:		Calculated Winding Parameters 		39

Table 5.2:		BEME							45

LIST OF FIGURES

Fig 2.1:	Feedback Oscillator Principle 				10

Fig 2.2:	Astable Multivibration Circuit 				11

Fig 2.3:	Symbol of an Enhancement Channel (MOSFET) 15

Fig 2.4:	 MOSFET Power Transistor Schematic		17

Fig 2.5:	Symobl of MOSFET 						17

Fig 3.1:	Block Diagram 						19

Fig 4.1:	Voltage Regulator/Monitor 				21

Fig 4.2:	UPS Circuit 							23

Fig 4.3:	Equivalent Circuit of T2 Showing the Origin of Overshoot 							24

Fig 4.4:	Cascaded Low Pass Filter 				25

Fig 4.5:	Pre-Amplifier 							26

Fig 4.6:	Buffer Amplifier 						28

Fig 4.7:	Darlington Pair Power Amplifier 			30

Fig 4.8:	Output Stage 							31

Fig 4.9:	Transformer Schematic Diagramme		33

Fig 4.10:	Transformer Turns Schematic Diagramme 	35

Fig 4.11:	Sketch of Transformer Core Lamination		41

CHAPTER ONE

INTRODUCTION

1.1	The Background of the Problem

Uninterrupted Power Supply (UPS) system is a unit developed for the conversion of direct current (DC) into alternating current (AC) to serve electronic and electrical appliances, such as radio sets, television sets, DVD/VCD, computer, photocopying machine etcetera and also provide lighting and power to fans. UPS systems could be used in conjunction with the solar energy conversion system for the harnessing of solar power energy and also as vital part of uninterrupted power surprise system.

The concept and development of UPS system because necessary of the poor national power supply system that resulted in incessant power supply and power outages. UPS is also found in use where there is no supply of electricity in the first place.

1.2	The Purpose/Objective/Aim of the Project

The purpose of the project is to design and construct a 1KVA UPS system for the supply of A.C power to serve load of about 800watts power (the active or real power, 1KVA x 0.8 = 800 watts).

The objective of the project is to ensure that the research produce an inverter and step-up transformer that would be able to transform few D.C voltage of about 12 voltage to up to 220 volt A.C 50Hz obtainable from the national power supply. Electronic appliances designed and constructed for use in Nigeria are meant to work at the designed specification of 220/230 Volt AC, 50Hz in contrast to similar equipment meant to work in a country like Japan whose national electric power supply is 110 volt A.C., 60Hz.

The designed and constructed UPS system in accordance with the specification of national power supply will not discriminate against any equipment nor serve only a particular electronic appliance. The UPS system will be universally accepted by any system operating in Nigeria or in countries that adopted same specification. By this, the aim of the project design and construction must have been achieved.

1.3	Scope of the Project

This project is on the design and construction of 1KVA UPS system with an in-built battery supply. In the first place, the 12 VDC battery is not part of the system to be designed implemented. The scope of the project includes designing and deriving the component values of all the circuits involved for the implementation of this project. These components are sourced and fixed in the vero board according to the determined circuitry, wired and tested through. The circuitry is completed by the design of transformer laminations and coils or windings, packaging and clamping of these laminations to air tight condition and testing through to ensure the specified rating of 1KVA which will supply a real power of 1KVA x 0.8.

The scope of the project also converted testing of the entire system after packaging in a metal construction with vent that will ensure in-let of air as coolant to the transformer that is expected to generate heat while in operation including power transistors.

The UPS system produced cannot work along wired installation of power supply from the national grid unless other units are incorporated. It works on stand alone bases where no power was extended from the national into operation intermittently.

1.4	Limitation of the Study

The major limitation in this project is seeking for a standard workshop with necessary tools for the cutting and packing of the laminations and coiling of the windings of the transformer. Sourcing exact values of designed and extracted components posed another serious challenge because the sellers of the components in the market only buy for part replacement by radio technicians and not mainly for research purposes.

Finally, finance posed a great problem in accomplishing this project since that task meant for four students was later carried out by only two students without reduction in capacity or in any form at all. Combination of the research activities coupled with normal classroom work, especially the graduating class, was of serious stress to the researchers.

However, at the end, a good job was achieved and those served as exposure to working under pressure, reminiscence of what could be expected in the field. We are seriously being prepared.

1.5	Definition of operational Terms:

Oscillator

An oscillator is an electronic device (circuit) designed to produce an alternating emf of desired frequency and amplitude from adc source without an external input.

Multivibrators

Multivibrators are class of oscillator that provide and output voltage of rectangular or square wave form. Three

Types of multivibrators are;

Astable (free running)

Monostable

Bitable    (or filp flop)

Abstable Multivibrators: is a type of multivariate that acts as an oscillator, and operation continuously to provide a rectangular waveform with particular values of phase repetition frequency.

Amplifier is a device that carry our signal amplification through a ration of change in output signal to a corresponding change in input signal with or without external connection.

Transistor is a semiconductor triode, called a bipolar function transistor, consisting of silicon (or germanium) crystal in which layer of n-type material is sandwiched between tow layers of p-type silicon to form P-N-P transistor. Alternatively, a transistor consist or a layer or p type between tow layers of n-type material to form an n-p-n transistor.

Mosfet Metal oxide semi conductor filed effect transistor (MOSFET) is a type of field effect transistor where increase in drain source voltage VDS do not produce prepositional increase in drain current ID. It operations on the principle of single pole charge carrier movement (hole or electron charge movement) as against bi-polar transistor where both hole and electron constitute the charge carrier in one form of transistor.

Report Organization

In conclusion to this chapter the mode of the organization of the report will be treated below.

In chapter one, the introduction of the system under implementation was treated. This included background of the project. The scope covered by the project was clearly stated and problems encountered that limited achievement by the researchers were also highlighted.

Chapter two handled review of related literatures to the project under consideration. These included the principles surrounding the major circuit implementation of the system as a lead to the actual circuits sourced for the system design.

Chapter three treated the design methodology, block diagram and actual design and derivation of components and their values. It was concluded by the joining of different circuits adopted into an overall circuit diagram of the system.

Chapter four was treated the system construction, testing and packaging. The outcome of the tests carried out was also discussed in this chapter.

Chapter five was a table that detailed the bill of engineering measurement and evolution. Simply, this was the listing of components and items deigned and sourced for, their prices and total price of the system costs. However, the summary, conclusion and recommend ion were discussed in chapter six to be followed on the rear by references and appendices.

CHAPTER TWO

LITERATURE REVIEW

UPS system is a concept from an oscillator circuit that produces output without an input. An oscillator therefore, is a device that produces an alternating output form a d.c sources, such as battery. An oscillator in effect, is an electronic circuit designed to product an’ alternating e.m.f. of desired frequency and wave form. The battery source provies biasing voltage to the active devices, transistors, amps, or Lcs serving as amplifiers. If part of the output of an amplifier, an active device, is feedback into the input in correct amplitude an phase, it is possible to obtain self-sustained oscillation. Any circuit may be made to oscillate, it is able to store and releases energy.

There is three- impedance oscillator type and feedback oscillator type. The principle adopted for the multivibrator employed in the design of the UPS circuit of this project is feedback oscillation.

Vin

Amplifier

Av

Vin Av

Vin Av

Frequency Determinacy Circuit

AVVin

Feedback

Network

2.1	Feedback Oscillator principle.

Fig. 2: 1 feedback oscillator

In the diagram above, the indicated Vin at the input is

In the diagram above, the indicated Vin at the input is not actually an external input signal to the amplifier but a fraction of the output voltage that was feedback to the input. The amplifier or the active device need only biasing or energizing voltage to release energy that is feedback in correct amplitude and phase.

Assuming the amplifier gain to be Av; the feedback factor; b; the output voltage being VinAv is passed through the feedback network to become BAVVin. To maintain oscillation;

Vin- B Vin AV = O

Vin ( - ABV) = O

But Vin = o and  - B Av = o

Therefore /ABV/=1 - - - - - 2.1

This is termed backhausen criterion, condition for unity loop gain for the substance of oscillation. The feedback factor B =

1

3.

Hence for the circuit to oscillate and be sustained, 1/3 of the amplifier gain need to be feedback to the input to ensure unite gain from the amplifier at all time.

2.2	Astable Multivibrator Principle

RL1

C2

C1

R2

R1

RL1

T2

T1

0/P2

0/P1

+ Vcc

Astable multivibrator circuit

An astable multivibrator also called ‘free running has the quality of an oscillator since it produce output without an input. It is a two stage RC amplifier with the output coupled back to the input. The feedback ratio (B = 1) is unity and positive because of the 180o phase shift in each stage, thus the circuit oscillates.

The circuit alternates between a state in which T1 is conducting and simultaneously T2 is cut- off and state in which T1 is cut-off and T2 is conducting. The transition between these two states is rapid because of the strong feedback signal. The time in each state depends. Upon resistor-capacitor time constant. During the conduction of T1, R1 and C1 determine the time constant while RL1 and transistor internal impendence with voltage drop VC2 along with Vcc determine the pulse with voltage drop VC2 along with Vcc determine the pulse amplitude. Also when T2 conducts, R2 conducts, R2 and C2 together with RL-2,

Transistor T2 internal resistance and voltage drop across c1

Determine the second pulse amplitude.

During the conduction of a transistor, the capacitor C1 or C2 charges to at least 2/3 of the supply voltage Vcc, hence

Vc1 = VC2 = Vc = Vcc (1 – (1 + B) e –t/Rc)

2 Vcc = Vcc (1- (1 – B) e – t/RC) -------2.2

3

For a circuit be oscillate and be sustained, the feedback factor B must be 1 of the output voltage.

3

2 Vcc = Vcc (1 – (1 + 1)  e-tRc)

3                               3

2 Vcc =Vcc (1- 2) e-trc)

3			3

2  = (1-2 e-tRc)

3          3

2   e –tRc = 1-2

3		  3

2 et/Rc   = 1 x 3 = 1

3	      3     2    2

Take natural logarithm

Line t/RC  in 0.5

- t/RC = - 0.693

- t = - 0.063 RC	-	-	-	-	-	2.3

t is the pulse width tw

… tw = 0.693 RC

The pulse amplitude is determined by peak over short voltage principle. The voltage drop across the coupling capacitor

Vc = Vcc x r	-	-	-	-	-	-	2.5

RL

Where; r is the internal resistance of the transistor whose value rages between 100 to 300 Ohms

Vc is the desired amplitude

RL is the load resistance and it equals

RL	=	Vcc x r	-	-	-	-	-	-	2.5

Vc

For a square wave, R1 = R2 = RL, = RL2 and are installed with variable resistors.

C1 = C2 and T1 = T2

2.3	Field Effect Transistor (FET)

FET is a voltage sensitive device which has extremely high input. Impedance as well as high output impedance. It is unipolar in natural because its operation depends on the movement of charge carriers of one polarity only; either hole for positive enhancement or electrons for negative enhancement mode relating to PNP and NPN respectively.

Drain D (Collector)

Gale G (Base)

Case

Source S Emitter)

Metal oxide semiconductor filed effect transistor (MOSFET) also called insulated gated field Effect Transistor (IGFET), is a type of FET where increases in drain – source voltage VDS do not produce proportional increase in drain current- ID but the value to 1o is prepositional to change in Gate- Source Voltage VGS.

Fig. 2.3 Symbol of an enhancement N- channel MOSFET

The MOSFET requires a positive gate voltage for N-channel enhancement mode. Increasing the gate voltage by allowing more current for enhancement increases the channel and this increases the channel conductivity.

Characteristics of MOSFET Power Transistors

1)	ECG 23 86, STM 320, MOSFET, N-Channel Enhancement, Hi Speed Switching, Transconductance gfs of 2 Mhos minimum, drain to source breakdown voltage BVDSS of 600 Volts minimum, gate to source break down voltage BVGS + 20 VMAX, continuous drain current ID = 6AMP, gate to source threshld voltage VGS (th) = 4.5 volts maximum, drain to source resistance RDS = 1.2 Ohms max, power dispation PD = 150W.

- ECG 2384, SSM6N 70, MOSFET N- Chanel, Enhancement, Hi-speed switch, transcnductance gfs of 1.8 Mhos Min, Drain to source breakdown voltage BVDSS = 800 volts min, Gate to source breakdown voltage BVGS = + 20v maximum, continuous drain current 1d = 6AMP, Gate to source Threshold voltage VGS (th) = 4 volts max, drain to source resistance RDS = 1.5 Ohms max, power Dispation PD …… watts.

Drain D (Collector)

Gate G

Sources

Fig. 2.4:	MOSFET Power Transistor Schematic

Drain

Gate

Source

Fig. 2.5: Symbole of MOSFET

CHAPTER THREE

DESIGN METHODOLOGY

Design and construction of 1KVA UPS system is a research and production of very important home and office use alternating current (AC) power supply for the use of electronic and electrical appliances. It is also capable of providing lighting to the rooms and environment.

The basis of some power system generation is extraction of .c voltage and use of same to harness and produce A.C. power regardless of current content. The low power a.c is now made to pass through several stages of power amplification and then through an inverter transformer to achieve 220/230 a.c volt at 50Hz. The capacity of the inverter transformer is the capacity of the power inverter system and this has to do with the output power expected and load also expected to carry.

1

2

3

4

5

6

7

8

3.1	Block diagram/flow chart of UPS

- Battery source

- Voltage Regulator/Monitoring/Indicators

- Inverter Circuit

- Filter

- Buffer/Pre-Amplifier

- Power Amplifier

- Inverter Transformer

- Output Socket

Fig. 3.1:	Power Inverter System Block Diagram.

3.2	Specification

The specification of the designed and constructed power inverter system is;

1.	Capacity 			=	1KVA

2.	Voltage  output 	=	220Volt A.C, 50Hz

3.	Current output 	=	12 Amps

4.	Transformer:		Step up, 10/220V A.C, 1 – 12 IV, 50Hz 500Hz, 127 turns, 16SWG

Single phase, VT = 1.739V, power Transformet.

CHAPTER FOUR

ANALYSIS AND DESIGN

Appropriate circuits with desired stability were sourced, adopted and component values of the parameters derived from the first principle. The block diagram of chapter three, Fig 3.1 were all determined and al components derived for purchase and actual construction. The end of this chapter will be an over all circuit diagram of the inverter system.

LM 7812

3

2

1k

GB

LED

C1

C2

1k

ZD

12V

RLY

Red LED

1k

Nc

4.1	Voltage Regulator/Monitor

Fig. 4.1:	Voltage Regulator/Monitor

This stage comprised an IC voltage regulator, LM7812 to ensure constant 12V voltage supply to the inverter circuit even when the battery voltage may not be 12V, hence ensuring stabilized output.

Capacitors C1 and C2 serve as fitters and d.c block ensuring that pure d.c voltage get to the inverter. Its impendence should be as low as 10Ohms and the inverter environment is 50Hz the national supply operating frequency.

As the output of the battery becomes so low that the regulator could no longer make it up to 12V output, the zener diode fails to continue being operated and the relay releases. The normal closed (NC) contact of the relay closes to extent current to the Red LED that now operates and indicate low batter voltage National.

∴C=12πfXc=12π x 50 x 10=0.000318

Capacitors C1 and C2 = 318µf

Standard capacitors close to this value are 220µf or 470µf. The former is selected hence C1 = C2 = 220µf (2). 1k Ohm is pull up resistor for the LED and Zener Diale and the Relay (3 number 1K ohms resistor).

12V relay

12V Zener Diode

+12v

C1

C2

R2

R3

R4

T2

T1

0/P1

0/P2

+ Vcc

VCC

R1

4.2	UPS Circuit

Fig 4.2:	UPS Circuit

Tw = 0.693RC 	-	-	-	-	-	-	-	-	3.1

Time constant t = tw 12f but f = 50Hz

:. Tw = 12 x 50=1100=0.01 seconds

Let C1 = C2 = C = 222 x 10-6 x R

R=0.010.693 x 220 x 10-6=66Ohms

:. R2 = R3 = 66 Ohms )2)

To determine the values of R1 and R4 also termed lad resistance RL. We shall employ peak overshot voltage. Principle, also to compute the voltage amplitude.

R4

T1

C4

R2

T2

V0

Vcc

Vcc

T1

C2

Fig 4.3: Equivalent circuit of T2 showing the origin of overshoot.

The voltage drop across the coupling capacitor gives the amplitude of the pulse wave

Vci=Vci=Vc=Vcc x rRL−−−−−−−−−−−−−−−3.2

Where Vcc is the supply voltage = 12V

r is the internal resistance of the transistor, taken to be 200Ώ

VC is drop at capacitor taken as IV

∴RL=R4=R1=Vcc x rVc=12 x 2001=2400=2.5kΩ

5k + variable resistor is adequate. To obtain a square wave, R1 = R2 = R3 = R4 = 5k variable resistors (4)

C1 = C2 = 220µf electroilytic capacitors (2)

Let T1 = T2 = TIP 27 = ECG 157 NPN, Si, Hv, AF, Pw Amp.

Component to ECG 39, PD = 20.8watts, FT = 10MHz, Ic = 5

Amp, BVEBO = 3V, BVCEO = 300v, BVCBO = 300v, hfe = 3- (gain).

4.3	Low Pass Filter

The pulse wave output of the inverter circuit contains some harmonics which resulted in the sharp ends or kinks and this constitute noise and not desirable since the inverter system can be used to power radio sets, TV or other sensitive appliances.

R2

R1

C1

C2

0/P

1/P

Hence, low pass filters are cascaded and connected at the outputs of the multivibrator called UPS circuit.

Fig. 4.4:	Cascaded Low Pass Filter

The filter is to pass frequency of 50Hz and cut off other frequencies above 50Hz, the national supply standard.

Fo=12πRC−−−−−−−−−−−−−−−−−−−−−−−−−−−−−−3.3

For a capacitor value of C1 = C2 = C = 220µF

R=12πfoC=12π x 50 x 220x10−6=15Ω

R1 = R2 = 15 ∴VT=1.12.5=1.739Volts (2), C1 = C2 = C220µF

4.4	Pre-Amplifier

+Vcc

T1

RB

C1

The pre-amplifier stage is a voltage amplifier stage to ensure that the voltage peak of the alternating voltage is up to at least IV. It is connected to Power Amplifier directly.

Fig. 4.5: Pre-Amplifier

Capacitor C1 serve as a coupling capacitor with low impedance of say 10Ohm

C1=12πfo x C=12π x 50 x 10−6=31.8μF

Capacity C1 = 220µf electrolytic. The base resistor R1 is to drop enough voltage that will open the transistor to conduct when supply voltage is applied to the collection terminal. Assuming 0.1mA current is coming from the output of the multivibrator through filter and the Vbe (base-emitter voltage) of the NPN transistor is 0.7V for silicon made the voltage drop at Rb taken as 0.9 V, hence

Rb=VbeIb=0.90.1 x 10-3=9000Ohms

Rb could be a 10KΏ resistor or any value between 7KΏ to 10kΏ

Rb	=	10KΏ

C1	=	220µf

T1	=	TIP 36, ECG 390, NON Si, Pwr Amp, HI speed complementary to ECG 391

BVCBO – BVCEO = 100v, Ic = 10A, BVCEO = 9V, PD = 60w, FT T 10MHz.

4.5	Buffer Amplifier

The buffer amplifier isolated the low power stage of the inverter circuit and high power amplifier stage. It is also termed unity gain amplifier or an emitter follower. It should come before pre-amplifier stage.

R1

R2

T1

C1

+Vcc

1/P

Vbe

Fig. 4.5:	Buffer Amplifier

Selecting T1 = BC 108, ECG 123A, NPN Si, AF Amp SW Vcbo = 40V, Vebo = 6, Ic = 8 Amps, PT = 50W, FT = 300 MHZ, hfe = 220.

VB = Vbe + IeR2

Ie=I1−α

:. Ve = IeRe substituting

Ve =Ib1−αRe−−−−−−−−−−−−−−−−−−−−−−−3.4

Voltage drop at Re = Vbe = Vce – Ve

Since Vbe for silicon = 0.7v and Vb = Ve

∴Ib=Vbe−VbQIbQ−−−−−−−−−−−−−−−−−−−−−−−−−3.5∴Ib=VeRp(1−α)

If Ve = Vbe = 0.7 volts, let Re = 300Ώ and α =  0.98

∴Ib=0.73001−0.98=0.7300 x 0.02=0.1167Amp∴Rb=12−0.70.1167=96.8≈1,00ΩRb=R1=100Ω

Capacitor C1 is a coupling capacitor and for an impedance of 10Ώ

C1=12πfoxC1=12πx50x10=31μ1C1=220μF

4.6	Power Amplifier

The power amplifier adopted to achieve desired current is a two stages Darlington pair push-pull power amplifier; to achieve a current of between 9Amp to 12Amp.

T1

T3

T2

T4

a

b

c

This Darlington pair power amplifier will be implemented by MOSFET power devices.

Fig 4.7:	Darlington pair power Amp.

The output of the pre-amplifier is connected to the gate of MOSFET T1 and T2. The pair of T1, T3 and T2, T4 release one shot pulse each (that was rounded off by the filter) to the UPS transformer to give a sinusoidal pure wave. The primary winding with the energizing current induce emf onto the secondary to prouce 220V, 50Hz A.C voltage of high current content.

T1 = T2 = SSM6N70, ECG 2384: PD = 125 W, ID = 6A, VGS = 4V, BVGS = 100V

T3 = T4 = STM320 = ECG 2386, Po = 150W, Io 6A,

BVGS = + 20V, VGS = 4.5V, BVOSS 600V.

R0

V

A

T1

C0

L0

0.1H

Socket

Fig 4.8: Output Stage

Capacitor Co is a paper capacitor for the storage and release of 220V, 50Hz A.C. voltage through the socket to the appliances or load. The inductor of 0.1H grows the induced emf to be collected by the plug into the socket.

Let Ro = 10Ω, Co = 100µF paper, Lo = 0.1H

4.7	Heat Sink

Heat sink inform of aluminum sheet are connected to the power transistor legs including the MOSFET to absorb heart released and radiated to the surrounding air that are let in through the vent provided at the casing to serve as coolant. The discharge of the heart helps in prolonging the life of the transistors/MOSFET; and in giving stabilized output voltage.

4.8	UPS Transformer Design

Transformer is the most important single component in this design and construction. The inverter transformer is a step-up transformer that transforms 12V AC from the power amplifier to 220V, 50Hz output. The transformer was designed constructed, packaged and tested through without humming or leakage.

Design Parameters

There are two types of transformers the core type and the shell type.

Core

Magnetic field

V1

N1

N2

I1

I2

V2

RL

V1

I1

I2

V2

Center Limb

(a) Core Type

(b) Shell Type

Fig 4.9:	Transformer Schematic Diagrams

In come type, the primary winding is on the left side of the core-limb while the secondary winding is on the right-hand side limb of the core. The magnetic field developed by current I1 applied on the primary coil through the core linked to the secondary winding on the other core arm of the right hand side. E.M.f. is thus induced and voltage V2 can be measured or developed across the load and current I2 flows.

However, fig 3.10(b) shows a shell type transformer where both primary and secondary coils are wound on the center limb but only separated with paper. Also through the core emf developed at the secondary output coil is due to magnetic field produced by current I1 at the primary coil. The paper is however impregnated with varnish or petroleum jelly.

Coefficient of Utilization

The coefficient of utilization or core factor C is the different ranges for different classes of transformers classified according to size and use.

Table 4.1:	Coefficient of Utilization

| S/N | Transformer Type | Core Factors C |
| --- | --- | --- |
| 1 | Three-phase, shell type | 1.3 |
| 2 | Three=phase, core type | 0.6 – 0.7 |
| 3 | Core distribution | 0.35 – 0.45 |
| 4 | Single-phase, shell type | 1.0 – 1.2 |
| 5 | Single-phase, core type | 0.75 – 0.85 |
| 6 | Core-type, power transformer | 0.55 – 0.65 |
| 7 | Shell-type, power transformer | 1 – 1.25 |

For this design and construction, a single phase shell type transformer was employed. The value of coefficient of utilization C is computed thus:  1.0+1.22=2.22=1.1

Therefore voltage per turn VT - VT=CKVA

a

b

c

-

+V

220V, 50Hz A/C

∴VT=1.12.5=1.739Volts

Fig. 4.10: Transformer Turns Schematic Diagram

In this inverter transformer design, the primary voltage is expected to be + 11 out of the 12 volts from the battery that  produced pulse or sinusoidal wave of about + 1 volt amplitude. The output is expected to be 22ov, 50Hz. A/C of around 12 Ampere current.

Primary turns Np

Np1  = v1(a) 	-	-	-	-	-	-	-	-	3.7

VT

Where Np1 is the turns of the primary that produce voltage V1(A)

V1 (a)  is the voltage at point (a-b) of the coil, which is 1.1

VT is the voltage per turn

…. Np1  = v1(a) = 11 = 6.3 6 turns

V1	1.739

But Np1= NP2 = 6 turns.

SECONDAY TURNS NS = N2

N2	=	V2 	-	-	-	-	-	-	-	(3.13)

VT

Expected output voltage is 22v

N2	=	220		= 126.5  127tursn

1.739

Diameter of copper wire

Copper wires are wound at current density of not greater than 100  Ampere/inch. 1 inch is equivalent to 2.54cm

Therefore,

X current in Amere/cm = 1000 Ampere/ cm

Area in cm2 			2.54cm

X current in Amp/cm x 2.54cm = Area in cm2 100/0/cm

Area = nr2 but r =  D .. Area = n (D)2    = Nd2

- 2          4

2. 54x current in Amp = 100 n D 2 Cm Amp

4

D2  =  4 (2.54) x current cm Amp

1000 n Amp

D2    =	10.6x current cm

1000n

Since the inverter will serve load of 5A to 15 Amp current, hence choosing 10A,   X current = 10 Amps

The winding diameter

D = 10.16 x 10

1000 n 		= 0.1798cm

Converting to millimeter

D = 0.1778 x 10 – 1.798

With this value, the standard wire gauge from the chart (SWG) is 15. SWG = 15 for primary of 6 turns. The primary coil is 6 turns, 15 SWG = 15 for primary of 6 turns. The primary coil is 6 turns, 15 SWG, 15A, 11 volts A.C.

Secondary

V2 = V2   = 22OV

Power: real power = Apparent x Power factor

= 500VA x 0.8 = 400W

Current in the secondary =  power

Voltage

Is = 2000 =  9.1 Amp

220

The coil diameter D = 10.16 X 9.1 = 0.17

1000  			= 0.17155

D = 0. 1716 cm

D = 0. 1716 x 10 = 1.716mm

From the standard wire gauge chart

SWG= 16

TABLE 4.2 calculated Winding parameter

| Terminal | Voltage | Current | Winding | Diameter | S.WG |
| --- | --- | --- | --- | --- | --- |
| Primary | 11V | 15 Amp | 6 turns | 1.798MM | 15 |
| Secondary | 220V | 9.1 Amp | 127 Turns | 1.716MM | 16 |

TRANSFOMER CORE DESIGN

Design parameters

D = diameter of circumscribing circle

H = Overall frame Height = 148mm

Aw = Winding Area

Ai = net iron area =  CSA of the core

W = Width of core widow = 42 mm

Wi = maximum width of lamination = 0.71d

F = Lamination stacking factor = 0.96

DT = Current density = 3  Amp/mm2

Kw = Winding space = 0.3

Bm = Flux density = 1.5T or 1.5 Wbs/m2, T= Testa.

Height of window to width of window ratio = 1:1

Type of limb section = square, 8 =3

Primary voltage vs  = 1 -12- 1 (11v)

Secondary voltage VS 220V

Transformer rating = 1KVA

Operation frequency f = 50Hz

Power factor = 0. 8 lagging

Power in watts = 800watts

Voltage per turn VT = 1.739 volts

Induced emf, E = 4.44 BMFAI per turn

Induced emf per turn VT = 4.44 BAMFAI

Ai = 		Vr 		=	1.739

4.4 Bmf 		4.44x1.5 x 50 m2

Ai    =    0.00522222222m2

Taking to mm2

Gross Area Ag	=	 Ai 			=	5222.22mm2

Stacking factor			0.96

Ag = 5440mm2

Transformer Core Construction

Fig 4.11: Sketch of a packaged transformer core limitation

148mm

42mm

18mm

160mm

14.8mm

42mm

Limitation core material is usually made of ferro-magnetic material characterized by high permeability, low cohesive force, low hystersis loss and high saturation induction. In has excellent magnetic current and less loss. The lamination core is cut in E and I shape out to the soft iron – sheet; and stacked together after varnishing and wrapped with paper to form a close iron pack magnetic circuit. The chosen shell type allows for al cooling paths for high efficient required for minimum heat dissipation. The lamination so packed is clamped and com[pressed to exclude all air.

Winding of the Transformer

The transformer core so packaged is wound with copper wired of the gauges obtained above and exactly to the number of turns. Copper is always used as the conductor material for winding because of its unique properties such as

- High electrical and thermal conductivity.

- Good mechanical properties.

- High resistance to corrosion

- High scrap value

- Readily available.

The primary winding is first wound covered with paper and then cooled with petroleum jelly before the secondary turns are wound on top varnished, coated and packaged with paper. Two terminals for the primary and secondary windings are brought out separately to serve as terminals. One cross sectional area of the core is prepared for fastening with screws.

Specifications

Transformer type: shell type, single phase, power square,

Core factor: 11

No of laminations: 38

Efficiency (Theorelicla): 80%

Voltage per turn: 1.739 volts

Transformer rating: 1KVA

Primary: centre tap: 1-2- IV, 50HZ, 10AMP, 6tunes, 15 SWG

Secondary: 22ov, 50 Hz 127 turns, 9.1Amp, 16 SWG.

4.9	COMPLETE CIRCUIT DIAGRAM OF 1KVA UPS SYSTEM WITH BUILT 12VDC BATTERY

CHAPTER FIVE

PRESENTATION AND ANALYSIS OF RESULT

Table 5: 1 BEME.

| S/N | Item (or component) | Rate in N | Qty | N Amount |
| --- | --- | --- | --- | --- |
| 1 | 22uf, 16V electrolytic capacitor | 50 | 12 | 600.00 |
| 2 | IK….. | 10 | 2 | 20.00 |
| 3 | LED (Green) (1) and Red (1) ), | 15 | 2 | 30.00 |
| 4 | 12 VDC Relay | 40 | 1 | 40.00 |
| 5 | 12v Zener Diode | 25 | 1 | 25.00 |
| 6 | 5kq variable Resistor | 20 | 4 | 80.00 |
| 7 | 15q Resistor | 10 | 4 | 40.00 |
| 8 | 100q Resistor | 10 | 2 | 20.00 |
| 9 | 300q Resistor | 10 | 2 | 20.00 |
| 10 | 10kq Resistor | 10 | 2 | 20.00 |
| 11 | 100uf paper capacitor | 20 | 1 | 20.00 |
| 12 | 10q Resistor | 10 | 1 | 10.00 |
| 13 | 0.1 H inductor | 20 | 1 | 20.00 |
| 14 | TIP 27 Transistor | 60 | 2 | 120.00 |
| 15 | BC 108 Transistor | 40 | 2 | 80.00 |
| 16 | TIP 36 Transistor | 80 | 2 | 160.00 |
| 17 | SSM 6N70 MOSFET | 250 | 2 | 500.00 |
| 18 | STM 320 MOSFET | 450 | 2 | 900.00 |
| 19 | Transformer Core Mould | 150 | 1 | 150.00 |
| 20 | Core Lamination | 1,600 | Set | 1,600.00 |
| 21 | Brown paper | 50.00 | 1 sq meter | 50.00 |
| 22 | Petroleum Jelly | 150 | 1 small cup | 150.00 |
| 23 | 15 SWG Cable | 25 | 20 meters | 500.00 |
| 24 | 16 SWG Cable | 20 | 20meters | 400.00 |
| 25 | Construction of metal box | 2,500 | 1 | 2,500.00 |
| 26 | 12” x 8” plank wood | 200 | 1 | 200.00 |
| 27 | Adhensive gum | 100 | 1 | 100.00 |
| 28 | Screw nails | 5 | 1 | 20.00 |
| 29 | Power switch | 50 | 1 | 50.00 |
| 30 | Wall socket | 70 | 1 | 70.00 |
| 31 | Socket base (wood) | 20 | 1 | 20.00 |
| 32 | Heat sink | 600 | ½ a mater sheet | 300.00 |
| 33 | Ammeter | 100 | 1 | 100.00 |
| 34 | Voltmeter | 100 | 1 | 100 |
| 35 | Labeling | - | - | 150.00 |
| 36 | 12 VD.C. battery | 4,500 | 1 unit | 4,500.00 |
|  |  |  |  | 13,615.00 |

Total cost is Thirteen thousand, six hundred and fifteen Naira (N13, 615.00).

5.1	Construction, Testing And Packaging

The derived component values as shown above in chapter three were taken to market for sourcing and purchased. The capacitors were determined during design process bearing in mind the standard values in the market. The resistor values purchased in most cease were those close in values to the values derived. Also purchased were breadboard also called project board for initial testing before actual connection and soldering was carried out in a verboard. Each component such as transistors and regulator were first tested to ascertain the collector electrode from emitter on the base electron for transistor and input and output pins for the regulator as different from the earth pin. All the capacitors are electrolytic and the positive and negative pins  have to be identified on the body of the capacitor. The colour coding helped for identification of the resistor values but the connection of the pins was never a concern since any of the two pins can be connected to any of the sides.

When the components were connected according to the circuitry, and tested through on project board, they were therefore unsocketed and fixed on the verboard solder the connection points avoiding dry joints and short circuits. Each circuit was connected and tested through before the next.

The transformer was specifically constructed as a specialized workshop where the laminations were cut and packaged on to the core mould according to the designed specification. A paper or plastic shaped core mould became a framework on to where the core laminations were layed, packaged, impregnated with varnishing or petroleum gelly and clamped together. The primary windings were first coiled on the core, exactly on the count of the designed number and coated with brown dry paper that was greased with petroleum gelly. The secondary windings were then wounded on top and counted to the number called SWG for both primary winding and secondary winding were sourced and purchased. At the end the constructed transformer was tested for vibration, humming, short circuit and disconnection.  Table 4. 1: Transformer Test.

The testing instrument employed for both transformer testing and wired circuit testing were AVO meter, battery. Continuity or resistance test was carried out when no voltage was connected to the circuit or system, static test.

Short circuit was tested both when no voltage was connected and when voltage was connected. Some circuit perform good when not connected voltage or when on load was connected and faulted when under dynamic condition.

The transformer was tested when not connected to voltage source, when voltage was connected and no load. A hundred watts bulb served as load when the test was been carried our under dynamic condition.

To assemble and package, a system box was constructed with vent openings to serve as coolant, letting in air to cool the transformer when in actual operation. A plant was cut and pressed down to the based of the system box and overboard (s) and the transformer base fastened on the wood. Indicators and switches was provided spaces but connected to the approximate parts of the system. And when the regulator can no longer upgrade the voltage to 12 V d.c for optimum operation of the inverter system. This monitor circuit comes into operation and incorporated to the regulator circuit to indicate low battery voltage. It reminds the user that the life of the battery has gone down too low and requires recharging or changing of electrolyte and charging again.

Below is the drawing of the packaged inverter system with in- built battery supply. The battery is held to the box with a belt and losen for charging or replacement.

DC

AC

OUT PUT

Fig 5.1: Compact 500VA power   Inverter system with in-built battery source

CHAPTER SIX

CONLUSION AND RECOMMENDATON

6.1	Conclusion

The design and construction of a 1KVA power inverter system with in- built battery source is a very important unit in the home of office for the supply of A.C power to the equipment, appliance and lighting installations. If found use in an area with out electric power supply or where national power supply is not satisfactory for the company of appropriate load as specified. This system went ahead of other known inverter system because of the- built batter source.

6.2	Recommendation

It is recommended for use by computer business centers, offices, in the villages where there is no electricity, in research institutions at out sketch of the city and in homes. It should be avoided to connect air conditioner or pressing iron on to the system except where all other loads were disconnected.

Any student venturing into the research and implementation of this system need to involve an automatic switching part and monitor so that it can be found useful where electricity is supplied but with ‘epileptic’ operation. The important part will make the UPS system operate like uninterruptible power supply for home or more load use as against the present used of UPS for a single appliance or equipment.

REFERENCES

Chiaginyi R & Eneh 1 (1999) Electronic Circuit Design Technique, Enugu: Hugotez Publications.

Horowitz P & Hill V. (1997) The Art of Electronic: Low Price Edition, N J, Princeton Press.

R.S. Component Ltd (1992) RS Component: International Edition, Califonia: MC Graw Coy.

Gibbs J. B. (1950) Transformer Principle and Practice: Second Edition New York: Mc Graw Hill Books Coy.

Philips E.C.G. (1998) Master Replacement Guide, New York: Philips.

Siemens Inc (1992) Crystal Locked DC to AC Power Converters Practical Wireless, Germany: Siemens Ltd.

Smith J. (1971) Circuit Devices and systems: 3rd Edition, London: Longman.

Texas Instruments Inc (1973) Transistor Circuit Design, Texas: MC Graw Hill Books Co. Inc.

American Power Conversion Crop. (1991) American Power Conversion Technical Note, New York: Power Conversion Corp.

APPENDIX

STANDARED WIRE GAUGE (S W G)  CHART

| S/N | Diameter in MM | Standard Wire Gauge (SWG) |
| --- | --- | --- |
| 1 | 8.230 | 0 |
| 2 | 7.620 | 1 |
| 3 | 7.010 | 2 |
| 4 | 6.6401 | 3 |
| 5 | 5.809 | 4 |
| 6 | 5.385 | 5 |
| 7 | 4.877 | 6 |
| 8 | 4.470 | 7 |
| 9 | 4.064 | 8 |
| 10 | 3.658 | 9 |
| 11 | 3.250 | 10 |
| 12 | 2.946 | 11 |
| 13 | 2.642 | 12 |
| 14 | 2.337 | 13 |
| 15 | 2.032 | 14 |
| 16 | 1.829 | 15 |
| 17 | 1.626 | 16 |
| 18 | 1.422 | 17 |
| 19 | 1.219 | 18 |
| 20 | 1.016 | 19 |
| 21 | 0.919 | 20 |
| 22 | 0.813 | 21 |
| 23 | 0.711 | 22 |
| 24 | 0.610 | 23 |
| 25 | 0.559 | 24 |
| 26 | 0.508 | 25 |
| 27 | 0.457 | 26 |
| 28 | 0.417 | 27 |
| 29 | 0.376 | 28 |
| 30 | 0.315 | 29 |
| 31 | 0.295 | 30 |
| 32 | 0.274 | 31 |
| 33 | 0.254 | 32 |
| 34 | 0.234 | 33 |
| 35 | 0.213 | 34 |
| 36 | 0.193 | 35 |
| 37 | 0.152 | 36 |
| 38. | 0.32 | 37 |

APPENDIX II

COLOUR CODE

0	-	Black

1	-	Brown

2	-	Red

3	-	Orange

4	-	Yellow

5	-	Green

6	-	Blue

7	-	Violet

8	-	Gray

9	-	White

Silver Tolerance 		=	5%

Gold Tolerance 		=	10%

Colorless				=	20%